

Abstract—This panel is the second in a series sponsored by the Distribution System Analysis Subcommittee  of the Power System Analysis Computing and Econonics Committee to establish reference cases for induction machine modeling for distribution system analysis of unbalanced three-phase systems. A simple 4-bus test case has previously been addressed. This test case is more strenuous and is based on the 34-bus test feeder case published by the committee.  It represents the placement of two large wind generators on a relatively weak rural distribution feeder.  The data for parameters added to the test case are described.  The test case consists of a power flow case and a single line-to-ground fault case. Results and modeling difficulties are discussed.

Induction Machine Test Case for the 34-Bus Test Feeder –Description

R. C. Dugan, Fellow, IEEE and W. H. Kersting, Fellow, IEEE

Index Terms – Power Distribution system analysis, induction machines.

# Nomenclature

R	Resistance

X	Reactance

Z	Complex impedance, R +j X

C 	Capacitance

Rs 	Stator Resistance

Xs	Stator Reactance

Rr 	Rotor Resistance

Xr 	Rotor Reactance

Xm 	Magnetizing Reactance

Is1, Is2	Positive and negative-sequence stator current

Ir1, Ir2	Positive and negative-sequence rotor current

(referred to stator)

# Introduction

THIS panel summary provides a description of the second in a series of induction machine test cases for three-phase distribution system analysis software. This test case has been developed by the Distribution System Analysis Subcommittee or the Power Systems Analysis, Computing and Economics Committee to provide a reference for developers to use to validate their models of induction machines under unbalanced conditions[1].

This subject is important because more large induction machines are being connected to distribution systems, requiring accurate models for planning purposes. One example would be wind turbines in sizes of more than 1 MW each and possibly installed in clusters of a few machines.

The Distribution System Analysis Subcommittee has been preparing a number of standard test feeders for benchmarking distribution system analysis programs. Distribution system analysts have had the capability to perform complete three-phase power flow and short circuit analysis for several years. However, benchmarks to validate the models were lacking.  Several basic test feeders have been developed. Each is designed to be challenging in some way for power flow and short circuit calculation algorithms. Stressing the algorithms in this manner is believed to be a good way to expose flaws in the methods and should result in more robust computer programs.

The next step was to develop test cases to validate a program’s capability to model various unbalanced transformer winding connections. A series of panels has been held on this subject. [2] - [7].

The latest series of panels is to provide benchmark s for induction machine models. This is an important issue because of the increase in the application in distributed generation technologies such as wind turbines and various combined heat and power applications that employ induction generators. This requires a more extensive model than many analysts have been using.  This test case takes the IEEE 34-node test feeder and adds two large induction machines that would be typical of wind generation. A power flow case and a short circuit case are described. The test case is confirmed with time domain simulation.

The most common method of modeling induction machine loads for distribution power flow is to simply assume a power and power factor, dividing the power equally among the phases. Motor load has been the primary focus of induction machine modeling. The error has been considered acceptable given the uncertainty in the other data available in distribution system analysis. However, with the need to analyze the voltage regulation effects of wind turbine generation comes the need for more accurate modeling.

Short circuit analysis of induction machine contribution varies. There are a few tools with detailed models. Others either neglect the contribution or model the machine as a voltage source behind transient reactance. Some assume that induction machine contribution to faults decays too quickly to matter. This might be true for three-phase faults, but the majority of faults are single line-to-ground. For these, the excitation level of the machines may change only slightly allowing it to continue to contribute current to short circuit faults. If the machine is especially large, as a wind turbine generator might be, the contribution can affect overcurrent protective relaying in a manner similar to other forms of distributed generation.

The plan for the continuing series of induction machine test cases is to consider such issues as power factor correction with switched capacitors, as is commonly done in wind turbine generators, and active rotor control of induction machines such as commonly done with doubly-fed induction machines. Those who are developing three-phase power flow and short circuit analysis tools are encouraged to move toward removing whatever barriers they might have in their software that prevent the accurate representation of induction generators.

# Test Case Description

Figure 1 shows the one-line diagram for the IEEE 34 Node Test Feeder with two additional induction generators, G1 and G2. This is a rather lengthy 24.9 kV feeder with a small 4.16 kV section. Two line voltage regulators are required to support the voltage under normal circumstances.  G1 is assumed connected at the end of one of the 24.9 kV laterals and G2 is connected to the end of the 4.16 kV system.

Fig. 2.  One-line diagram of 34-bus test feeder system with two induction generators, G1 and G2.

The basic data for the Test Feeder can be downloaded from:

http://ewh.ieee.org/soc/pes/dsacom/testfeeders.html

Two three-phase induction generators with step-down transformers have been added to the feeder for the purpose of testing induction generator models.  The data for the transformers and generators are as follows:

Generator G1 and G2 Data:

Power out: 660 kW

Rated voltage:  480 volts

Impedance Data:

- Rs = 0.0053 per-unit

- Xs = 0.106 per-unit

- Rr = 0.007 per-unit

- Xr = 0.120 per-unit

- Xm = 4.0 per-unit

Note:  The per-unit impedance values are based upon 660 kVA and 480 (L-L) volts.

Both generators are assumed to be simple induction machines for the purposes of this test case.  No power factor correction capacitors are included in this example. Power factor correction will be investigated in future test cases.

Transformer T1 and T2 Data

T1:

750 kVA,

24.9 / 0.48 kV,

Z = 1 + j5 %

T2:

750 kVA,

4.16 / 0.48 kV,

Z = 1 + j5 %

There are some things in the 34 Node Test Feeder that the reader should take caution to properly represent:

- The impedance matrices for three-phase line types 300 and 301 are given in the phase order of ABC  (or 123, if you prefer). A casual reading of the test case document might cause one to conclude the order is BAC, which is the physical order of the phases on the crossarm.

- When a load is specified as delta (designated D) on phase 1, it is assume connected from phase 1 to 2. Likewise, delta loads on phases 2 and 3 are connected 2 to 3 and 3 to 1, respectively.

# Power Flow Case Results

In this paper, which is a summary of the panel, selected results of the base case snapshot power flow are presented.

These results were computed using an iterative three-phase power flow solution in the steady state.

From a flat start of 1.0 per unit voltages, a total of 81 iterations was required to converge to a tolerance of 0.0001 per unit. This includes the tap changer simulations in which the solution is fully converged before computing another tap position. The maximum number of iterations at any tap position was 28.

Table i.
 Selected Phase-to-Neutral Voltages

| Bus | Phs | VL-N, kV | Angle, deg | Per unit |
| --- | --- | --- | --- | --- |
| 800 | 1 | 15.094 | 0 | 1.0499 |
| - | 2 | 15.094 | -120 | 1.0499 |
| - | 3 | 15.094 | 120 | 1.0499 |
| 802 | 1 | 15.07 | 0 | 1.0482 |
| - | 2 | 15.08 | -120 | 1.0489 |
| - | 3 | 15.084 | 120 | 1.0492 |
| 808 | 1 | 14.748 | 0.4 | 1.0258 |
| - | 2 | 14.918 | -119.8 | 1.0377 |
| - | 3 | 14.959 | 120.4 | 1.0405 |
| 810 | 2 | 14.916 | -119.8 | 1.0375 |
| 814 | 1 | 14.104 | 1.3 | 0.98104 |
| - | 2 | 14.619 | -119.4 | 1.0169 |
| - | 3 | 14.696 | 121.4 | 1.0223 |
| 814reg | 1 | 14.632 | 1.3 | 1.0178 |
| - | 2 | 14.71 | -119.4 | 1.0232 |
| - | 3 | 14.696 | 121.3 | 1.0222 |
| 850 | 1 | 14.632 | 1.3 | 1.0178 |
| - | 2 | 14.71 | -119.4 | 1.0232 |
| - | 3 | 14.696 | 121.4 | 1.0222 |
| 816 | 1 | 14.629 | 1.3 | 1.0176 |
| - | 2 | 14.708 | -119.4 | 1.0231 |
| - | 3 | 14.695 | 121.4 | 1.0221 |
| 824 | 1 | 14.572 | 1.6 | 1.0136 |
| - | 2 | 14.635 | -119.2 | 1.018 |
| - | 3 | 14.649 | 121.5 | 1.019 |
| 822 | 1 | 14.23 | 1.2 | 0.98984 |
| 826 | 2 | 14.633 | -119.2 | 1.0178 |
| - | 2 | 14.633 | -119.2 | 1.0178 |
| - | 3 | 14.647 | 121.5 | 1.0188 |
| 854 | 1 | 14.455 | 2.2 | 1.0055 |
| - | 2 | 14.51 | -118.8 | 1.0093 |
| - | 3 | 14.549 | 121.9 | 1.012 |
| 832 | 1 | 14.817 | 3.3 | 1.0307 |
| - | 2 | 14.843 | -118 | 1.0325 |
| - | 3 | 14.843 | 122.5 | 1.0324 |
| 858 | 1 | 14.802 | 3.4 | 1.0296 |
| - | 2 | 14.824 | -118 | 1.0312 |
| - | 3 | 14.829 | 122.5 | 1.0315 |
| 834 | 1 | 14.784 | 3.4 | 1.0284 |
| - | 2 | 14.803 | -118 | 1.0297 |
| - | 3 | 14.814 | 122.5 | 1.0304 |
| 836 | 1 | 14.775 | 3.4 | 1.0277 |
| - | 2 | 14.792 | -118 | 1.0289 |
| - | 3 | 14.807 | 122.5 | 1.0299 |
| 840 | 1 | 14.775 | 3.4 | 1.0277 |
| - | 2 | 14.791 | -118 | 1.0289 |
| - | 3 | 14.806 | 122.5 | 1.0299 |
| 848 | 1 | 14.806 | 3.4 | 1.0299 |
| - | 2 | 14.816 | -118 | 1.0306 |
| - | 3 | 14.836 | 122.5 | 1.0319 |
| 856 | 2 | 14.508 | -118.8 | 1.0092 |
| 852 | 1 | 14.282 | 3.3 | 0.99343 |
| - | 2 | 14.307 | -118 | 0.99517 |
| - | 3 | 14.393 | 122.5 | 1.0012 |
| 852reg | 1 | 14.817 | 3.3 | 1.0307 |
| - | 2 | 14.843 | -118 | 1.0325 |
| - | 3 | 14.843 | 122.5 | 1.0324 |
| 864 | 2 | 14.824 | -118 | 1.0311 |
| 838 | 2 | 14.789 | -118.1 | 1.0287 |
| 890 | 1 | 2.2853 | 11.7 | 0.95147 |
| - | 2 | 2.2743 | -110.1 | 0.94689 |
| - | 3 | 2.2901 | 130.7 | 0.95346 |
| G1 . | 1 | 0.28158 | 6 | 1.016 |
| - | 2 | 0.28143 | -115.3 | 1.0155 |
| - | 3 | 0.28244 | 125.2 | 1.0191 |
| G2 . | 1 | 0.25925 | 14.8 | 0.93546 |
| - | 2 | 0.25769 | -106.9 | 0.92983 |
| - | 3 | 0.26013 | 133.8 | 0.93862 |

Table II 
Selected Currents INTO Circuit Element Terminals 
at Indicated Bus

| Bus | Phase | Amperes | Ang., deg |
| --- | --- | --- | --- |
| Line 800-802 |  |  |  |
| 800 | 1 | 32.477 | -54.3 |
| 800 | 2 | 25.431 | -178.6 |
| 800 | 3 | 18.833 | 60.8 |
| 800 | Residual | 10.928 | 104.4 |
| Line 850-816 |  |  |  |
| 850 | 1 | 32.899 | -56 |
| 850 | 2 | 24.022 | 174.3 |
| 850 | 3 | 18.757 | 55.5 |
| 850 | Residual | 10.717 | 118.5 |
| Line 854-852 |  |  |  |
| 854 | 1 | 22.286 | -77.5 |
| 854 | 2 | 21.758 | 165.6 |
| 854 | 3 | 18.109 | 50.6 |
| 854 | Residual | 5.2836 | 26.1 |
| Generator G1 |  |  |  |
| G1 | 1 | 856.37 | -147.3 |
| G1 | 2 | 891.82 | 92 |
| G1 | 3 | 866.31 | -29.7 |
| Generator G2 |  |  |  |
| G2 | 1 | 943.55 | -137.9 |
| G2 | 2 | 975.29 | 100.8 |
| G2 | 3 | 941.78 | -20.2 |

Table III 
Generator Solution

| Quantity | Value | Unit |
| --- | --- | --- |
| G1 |  |  |
| Slip | -0.00751 |  |
| Is1 | 871.371 | A |
| Is2 | 21.2034 | A |
| Ir1 | 825.162 | A |
| Ir2 | 20.5858 | A |
| Stator Loss | 4216.96 | W |
| Rotor Loss | 4994.67 | W |
| G2 |  |  |
| Slip | -0.00912 |  |
| Is1 | 953.413 | A |
| Is2 | 21.9022 | A |
| Ir1 | 909.999 | A |
| Ir2 | 21.2643 | A |
| Stator Loss | 5048.09 | W |
| Rotor Loss | 6074.03 | W |

Table IV 
Regulator Solution

| Reg / Phase | Tap, pu | Position |
| --- | --- | --- |
| 814 - 850 |  |  |
| 1 | 1.0375 | 6 |
| 2 | 1.00625 | 1 |
| 3 | 1 | 0 |
| 852 - 832 |  |  |
| 1 | 1.0375 | 6 |
| 2 | 1.0375 | 6 |
| 3 | 1.03125 | 5 |

# SLG Fault Case

In most distribution system analysis programs, the short circuit currents are computed in the steady state. This has always presented a problem for cases with large rotating machines because the fault current does not stay constant with time. For induction machines, many assume a worst case in which the machine is represented similarly to synchronous machines as a voltage behind either transient or subtransient reactance. There are two currents of interest:

- The current in the first half cycle that can impact breaker momentary ratings and fuse melting times.

- The current a few cycles later when breakers and fuses are attempting to interrupt the current.

The induction machine contribution to a nearby three phase fault usually decays quite rapidly because the excitation largely disappears. If the machine is where the voltage sag is not so great, the contribution can continue. A conservative rule of thumb states that if the voltage remains above 60%, one should treat the induction machine as if it were a synchronous machine. The panelists modeling the test feeder in the time domain will provide greater detail on this issue.

# Acknowledgment

The authors gratefully acknowledges the contributions of Tom McDermott, Surya Santoso, and Jean Mahseredjian to the development of this test case.

# References

- IEEE PES Distribution Systems Analysis Subcommittee Radial Test Feeders, http://ewh.ieee.org/soc/pes/dsacom/testfeeders.html.

- R. C. Dugan, “A Perspective on Transformer Modeling for Distribution Systems Analysis,” IEEE PES General Meeting Conference Proceedings, Toronto, July 2003

- R.C Dugan and S. Santoso, “An Example of 3-phase Transformer Modeling for Distribution System Analysis,” 2003 IEEE PES Transmission and Distribution Conference Proceedings, Dallas, September 2003.

- W. Kersting, “Center Tapped Wye-Delta Transformer Bank Test Case,” 2004 IEEE PES General Meeting Conference Proceedings, Denver, June 2004.

- R.C. Dugan, “Experiences with Center-Tapped Wye-Delta Transformer Test Case,” 2004 IEEE PES General Meeting Conference Proceedings, Denver, June 2004.

- W. Kersting, “Analysis of Four Wire Delta Center Tapped Transformer Connections,” 2005 IEEE PES General Meeting Conference Proceedings, San Francisco, June 2005.

- R.C Dugan and S. Santoso, “Experiences with the New Open-Wye / Open-Delta Transformer Test Cases for Distribution System Analysis,” 2005 IEEE PES General Meeting Conference Proceedings, San Francisco, June 2005.

# Biographies

Roger C. Dugan (F '00) is Sr. Consulting Engineer for EPRI Solutions, Inc, Knoxville, TN.  He holds the BSEE degree from Ohio University and the MEEPE degree from Rensselaer Polytechnic Institute, Troy, NY.  He was previously a Sr. Consultant with Electrotek Concepts, Knoxville, TN and Sr. Staff Engineer in the Systems Engineering department of McGraw-Edison Power Systems, now Cooper Power Systems.  Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. He was elected a Fellow for his contributions in harmonics and transients analysis.  Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems.  He conducts workshops on distribution planning with distributed generation. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, 2nd edition.  He serves on IEEE PES Distribution System Analysis Subcommittee and is currently Vice-Chair of the Power Systems Analysis, Computing, and Economics Committee.

W. H. Kersting (SM’64, F’89) was born in Santa Fe, NM.  He received the BSEE degree from New Mexico State University, Las Cruces, and the MSEE degree from Illinois Institute of Technology.  He joined the faculty at New Mexico State University in 1962 and served as Professor of Electrical Engineering and Director of the Electric Utility Management Program until his retirement in 2002.  He is currently a consultant for Milsoft Utility Solutions.  He is also a partner in WH Power Consultants, Las Cruces, NM.

R. C. Dugan is with the EPRI Solutions, Inc, Knoxville, TN 37923 USA (e-mail: r.dugan@ieee.org).

W. H. Kersting is a consultant and partner with WH Power Consultants, Las Cruces, NM (e-mail: bjkersting@zianet.com)