

Abstract—This panel summary presents the time-domain modeling of a distribution system where two wind turbines are interconnected.  The distribution system is based on the IEEE 34-bus test feeder.  The panel summary details the modeling of a wind turbine and analyzes the system power flow.  Both modeling and power flow analysis are performed in the time-domain.

Induction Machine Test Case for the 34-Bus Test Feeder: A Wind Turbine Time-domain Model

Surya Santoso, Zheng Zhou

Index Terms—Power distribution system analysis, induction machines, electromagnetic transient, modeling and simulation.

# Introduction

WIND power has become an important energy source in recent years.  According to the U.S Energy Information Administration in its latest Annual Energy Review (2004), the electricity net generation from wind resources grew by more than 320% in the past ten years i.e. from 3.4 to 14.2 billion kWh [1].  This trend is likely to continue especially with various economic incentives at the state and federal levels.  For example, the recent 79th Texas Legislatures renewed the 1999 Renewable Portfolio Standard and calls for a cumulative installed renewable capacity of 5,880 MW (approximately 13.5% of the anticipated statewide electric energy generation in by January 1, 2015) and 10,000 MW (approximately 16% of the anticipated statewide electric energy generation in January 1, 2025) [2].  The 1999 Renewable Portfolio Standard set a goal of 2000 MW of new generating capacity from renewable sources or a cumulative installed renewable capacity of 2,880 MW by 2009.

The majority of installed wind energy facilities is located at excellent wind sites (i.e., class 4 – 5) and interconnected at the transmission voltage level.  A typical nameplate rating of a recently installed transmission-level wind turbine is 1.5 MW and higher.  However, as the wind turbine technology matures,  smaller wind turbines can also be found at the distribution voltage level, i.e., between 12.47 kV and 34.5 kV.  Impacts of wind power on distribution systems are likely more significant than those at the transmission level.  This is due to the fact that distribution systems are weaker.  A large wind speed variation can cause significant feeder voltage variations.  Voltage regulators may have swung from one end of the tap to another in an attempt to hold to voltage at the prescribed level.

A distribution system study, power flow, feeder voltage regulation, and short-circuit analysis, becomes necessary for planning and evaluating the suitability and impacts of wind power generation in the distribution system.  Therefore, the objective of this summary is to present load flow and short-circuit results of an IEEE 34-bus test feeder having two induction generators using a time-domain modeling approach.  The results will be used to validate and benchmark those obtained using the steady-state distribution system analysis which is currently being carried out.

This panel summary first describes the time-domain modeling [3-4] of the IEEE 34-bus test feeder and the associated load flow results in Section II.  The results will be compared to those of [5] to establish an accurate base case.  Section III presents an overview of wind generator modeling, while Section IV describes the load flow and short-circuit analysis of the time-domain test feeder.  The analysis results are expected to serve as a benchmark to other steady-state approaches [6].

# Time-Domain Modeling of 
the IEEE 34-bus Test Feeder

For the purpose of validating induction machine models for steady-state distribution system analysis, the IEEE 34-bus test feeder and induction machine models are represented in the time-domain [7-8].  The oneline diagram of the test feeder with two induction generators is illustrated in Figure 1.

Fig. 2.  One-line diagram of 34-bus test feeder system with two induction generators, G1 and G2

Feeders in the test system are unbalanced.  Therefore, an unbalanced feeder is represented with a phase impedance matrix.  The shunt capacitance of overhead and underground lines is included as well.

Load models are represented accordingly with constant PQ, constant impedance, and constant current in the wye or delta configuration.  A distributed load is represented with the so-called exact lumped load model; thus one-third of the load is placed at the end of the line, while two-thirds of the load is placed at one-fourth of the way from the source end [9].

Results of the load flow analysis are shown in Table 1 and will be compared with those of [10].  Note these results are based on fixed regulator tap positions and without any induction generators.

Table 1:  Load flow results

|  | Node Voltage pu |  |  |
| --- | --- | --- | --- |
| Node | A-N | B-N | C-N |
| 800 | 1.05 | 1.05 | 1.05 |
| 802 | 1.047 | 1.048 | 1.048 |
| 806 | 1.046 | 1.047 | 1.047 |
| 808 | 1.014 | 1.03 | 1.029 |
| 810 |  | 1.029 |  |
| 812 | 0.9769 | 1.01 | 1.006 |
| 814 | 0.9474 | 0.9943 | 0.9887 |
| 850 | 1.018 | 1.025 | 1.02 |
| 816 | 1.018 | 1.025 | 1.019 |
| 818 | 1.017 |  |  |
| 820 | 0.9941 |  |  |
| 822 | 0.9912 |  |  |
| 824 | 1.009 | 1.016 | 1.011 |
| 826 |  | 1.016 |  |
| 828 | 1.008 | 1.015 | 1.01 |
| 830 | 0.9903 | 0.998 | 0.9929 |
| 854 | 0.9898 | 0.9976 | 0.9925 |
| 852 | 0.9589 | 0.9678 | 0.9627 |
| 832 | 1.037 | 1.034 | 1.035 |
| 858 | 1.034 | 1.032 | 1.033 |
| 834 | 1.032 | 1.029 | 1.03 |
| 842 | 1.032 | 1.029 | 1.03 |
| 844 | 1.031 | 1.029 | 1.03 |
| 846 | 1.032 | 1.029 | 1.03 |
| 848 | 1.032 | 1.029 | 1.03 |
| 860 | 1.031 | 1.029 | 1.03 |
| 836 | 1.031 | 1.028 | 1.03 |
| 840 | 1.031 | 1.029 | 1.03 |
| 862 | 1.031 | 1.029 | 1.03 |
| 838 |  | 1.028 |  |
| 864 | 1.034 |  |  |
| 888 | 0.9961 | 1.004 | 0.9962 |
| 890 | 0.9134 | 0.9294 | 0.9138 |
| 856 |  | 0.9976 |  |

# Modeling of Wind Induction Generators

A wind turbine is an electromechanical energy conversion device that captures kinetic energy from wind and turns it into electrical energy.  Therefore, for the purpose of modeling a wind turbine, it needs to include the following: wind source model, aerodynamic model of the wind turbine rotor, mechanical model of the gearbox system, and finally an electric machine and its associated power and speed controls.

During the panel presentation, the wind turbine model based on the fixed speed stall regulated technique will be presented.  The wind speed quantity will be adjusted to produce the desired wind power as required by the test case.  The response of the wind turbine to single-line and three-phase faults will be influenced by the rotor as well as the induction machine inertias.

# Discussions

During the panel presentation, results from the base test case (i.e., without the two wind generators) will be compared and presented.  Simulation and modeling of wind turbines will be described.  Finally, we will discuss the response of the wind turbine to single-line and three-phase faults.

# References

- Annual Energy Review 2004, DOE/EIA-0384 (2004), Aug. 2005.

- Section 3 (Section 39.904) of Senate Bill 20, the 79th Texas Legislature, July 14, 2005, Austin, TX

- PSCAD User’s Guide, Manitoba HVDC Research Centre, Winnipeg, Canada. .

- EMTDC Transient Analysis of PSCAD Power System Simulation User’s Guide, Manitoba HVDC Research Centre, Winnipeg, Canada.

- IEEE Distribution System Analysis Subcommittee, IEEE 34 Node Test Feeder, http://ewh.ieee.org/soc/pes/dsacom/testfeeders.html.

- R.C Dugan, “Induction Machine Test Case for the 34-Bus Test Feeder: Description”, this Conference Proceedings.

- W.H Kersting, Distribution System Modeling and Analysis, CRC Press, 2002.

# Biographies

Surya Santoso (SM '02) has been Assistant Professor with Department of Electrical and Computer Engineering, The University of Texas at Austin since 2003.  He was a Sr. Power Systems/Consulting Engineer with Electrotek Concepts, Knoxville, TN between 1997 and 2003.  He holds the BSEE degree from Satya Wacana Christian University, Indonesia, and the MSEE and Ph.D degrees from the University of Texas at Austin.  His research interests include power system analysis, modeling, and simulation.  He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 2nd edition. He chairs a task force on Intelligent System Applications to Data Mining and Data Analysis, and a member of the IEEE PES Power Systems Analysis, Computing, and Economics Committee.

Zheng Zhou received her B.Sc from Southeast University in 1988 and M.Sc. degree from the University of Manitoba in 2003.  Presently she is employed by the Manitoba HVDC Research Centre.  Her research area is in power system, digital simulation and power electronics. She is a registered Professional Engineer with the Province of Manitoba.

S. Santoso is with Department of Electrical and Computer Engineering, The University of Texas at Austin, Austin, TX 78712.

D. Muthumuni and Z. Zhou are with Manitoba HVDC Research Centre, Winnipeg, Manitoba, Canada.